## EXAMPLE
FAN Brand | Best Maker Ever
Model Number | FastFan2000 | [8 empty] | System Curve Line, for graphic only
PURCHASED FOR Moving Air Fast! | [9 empty] | zero | 0 | 0
[10 empty] | Point 1 | 3039.9875 | 5.1497 | Existing curve
STEP 1: Populate Chart | [9 empty] | Point 2 | 1339.6226 | 1 | NEW point (TC)
Read data from the chart profided by the manufacturer. | [9 empty] | Power Curve Line, for graphic only
[10 empty] | zero | 1339.6226 | 0
[10 empty] | System Curve | 1339.6226 | 1
Chart RPM (n1) |  | 3136 | [7 empty] | S.P. Curve | 1339.6226 | 6.8692
Chart Temperature (°F) |  | 250 | [7 empty] | Power Curve | 1339.6226 | 2.6053
Maximum rated RPM |  | 3460 | [7 empty] | Chart Labels
Maximum Rated Temperature (°F) |  | 800 | [7 empty] | Title | Best Maker Ever FastFan2000
Motor Power (Hp) |  | 7.5 | [7 empty] | x - axis | Flow Rate (ACFM @ 250°F)
Blower Outlet Area (ft2) |  | 1.3 | [7 empty] | y - axis | S.P. (in wg)
ACFM @ 250°F | SP (in. wg) | Power (Hp)
0 | 6.2 | 1.25
500 | 6.6 | 1.75
1000 | 6.9 | 2.4
1500 | 7 | 2.7 | STEP 2: Populate Table of Coefficients |  |  |  |  | RESULTS
2000 | 6.65 | 3.15 | Use best fit trendlines to determine the equations describing power and pressure curves. |  |  |  |  | Includes Temperature Correction
2500 | 6 | 3.45 | [5 empty] | Flow rate ACFM (Q3) | 1339.6226
3000 | 5.25 | 3.8 | Table of Coefficients (A = highest power) |  |  |  |  | Pressure (P2) | 1
3500 | 4.1 | 3.9 |  | A | B | C | D | Rpm (n3) | 1381.9322
4000 | 2.8 | 3.75 | S.P. (P1) | -4.8298e-07 | 0.001104 | 6.257 |  | BHP3 | 0.43185
4500 | 1.2 | 3.5 | Power | -3.7918e-11 | 6.2704e-08 | 0.00098162 | 1.2689 | Outlet Ft/m (Actual) | 1030.479
5000 | 0 | 3 | Note: solving for Q1 is easiest when S.P is quadratic |  |  |  |  | (red text is over limit)
|  |  | Step 3: Specify new Operating point |  |  |  |  | Step 5: Optional Inputs |  | Inlet Conditions
|  |  | Flow rate {SCFM} (Q2,std.) |  |  |  | 1000 | Dryer Bed Length (ft) | 5 | Inlet Temperature (°F,°C) |  | 45 | 7.2222
|  |  | Operating S.P. {inH20} (P2) |  |  |  | 1 | Dryer Bed Width (ft) | 2 | Inlet Diameter (Inch, m) |  | 20 | 0.508
|  |  | Operating Temp {°F} |  |  |  | 250 | Dryer Bed Area (ft2) | 10 | Inlet Area (ft2, m2) |  | 2.1817 | 0.20268
[8 empty] | Free Stream V (AFPM) | 133.9623 | Density Factor (Kd) |  | 0.95283
|  |  | Step 4: Calculate System Curve Intersection |  |  |  |  | Free Stream V (m/s) | 0.68053 | Inlet Volumetric flow (SCFM, SLPS) |  | 1000 | 471.9467
|  |  | From the System curve relationship (Eq. 1), solve for the flow rate in SCFM on the original fan curve (Q1). Recall that the static pressure (P1) on the original fan curve is give as a function of Q1 using the equation from Step 2. Use temperature corrected to flow rate for these calculations For example: If the pressure equation is quadratic and the power curve is cubic, then Q1 = (-B - sqrt(B2 - 4(A-P2/Q22)C) )/ 2(A-P2/Q22) P1 = AQ12 + BQ1 + C BHP1 = AQ13 + BQ12 + CQ1 + D | [6 empty] | Inlet Volumetric flow (ACFM, ALPS) |  | 952.8302 | 449.685
[10 empty] | Inlet Velocity (FPM, MPS) |  | 436.7452 | 2.2187
[8 empty] | Intermediate State |  | Inlet mass flow (lbs/s, kg/s) | Inlet Mass Flow (kg/s, lbs/s) | 1.253 | 0.56835
Includes Temperature Correction
[8 empty] | Density Factor (Kd,1-2) | 0.74648
[8 empty] | Density Factor (Kd,2-3) | 1.3396
(red text is over limit)
|  |  | Flow rate CFM (Q2,chart) |  |  | 1339.6226
|  |  | P2/Q22 |  |  | 5.5723e-07
|  |  | Q1,chart |  |  | 3039.9875
|  |  | P1,chart |  |  | 5.1497
|  |  | BHP2,chart |  |  | 3.7672
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
Eq. 2: Rpm - flow relationship (41.22)
Eq. 3: Rpm - Pressure relationship (41.23)
Eq. 4: Rpm- Power Relationship (41.25)
Eq. 5 Density factor (absolute Temp) (41.2)
Eq. 6 Density flow change (41.1)
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
𝑃_1/𝑃_2 =(𝑄_1/𝑄_2 )^2
Eq. 2: Rpm - flow relationship (41.22)
𝑛_1/𝑛_2 =𝑄_1/𝑄_2
Eq. 3: Rpm - Pressure relationship (41.23)
(𝑛_1/𝑛_2 )^2=𝑃_1/𝑃_2
Eq. 4: Rpm- Power Relationship (41.25)
(𝑛_1/𝑛_2 )^3=〖𝐵𝐻𝑃〗_1/〖𝐵𝐻𝑃〗_2
Eq. 5 Density factor (absolute Temp) (41.2)
𝐾_𝑑=𝜌_𝑠𝑡𝑑/𝜌_𝑎𝑐𝑡 =𝜌_1/𝜌_2 =(𝑃_1/𝑃_2 )×(𝑇_2/𝑇_1 )
Eq. 6 Density flow change (41.1)
𝑆𝐶𝐹𝑀=𝐴𝐶𝐹𝑀/𝐾_𝑑
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
- Static Pressure (In w.g.)
- Power (HP)
- System Curve
- Power Intersection

## Hartzel A03-9-152BC-75STFCM2
FAN Brand | Hartzel
Model Number | A03-9-152BC-75STFCM2 | [8 empty] | System Curve Line, for graphic only
PURCHASED FOR USDA 2015 DRYER PHASE II | [9 empty] | zero | 0 | 0
[10 empty] | Point 1 | 4755.1041 | 0.58592 | Existing curve
STEP 1: Populate Chart | [9 empty] | Point 2 | 4364.717 | 0.49366 | NEW point (TC)
Read data from the chart profided by the manufacturer. | [9 empty] | Power Curve Line, for graphic only
[10 empty] | zero | 4364.717 | 0
[10 empty] | System Curve | 4364.717 | 0.49366
Chart RPM (n1) |  | 3136 | [7 empty] | S.P. Curve | 4364.717 | 1.8745
Chart Temperature (°F) |  | 250 | [7 empty] | Power Curve | 4364.717 | 3.595
Maximum rated RPM |  | 3460 | [7 empty] | Chart Labels
Maximum Rated Temperature (°F) |  | 800 | [7 empty] | Title | Hartzel A03-9-152BC-75STFCM2
Motor Power (Hp) |  | 7.5 | [7 empty] | x - axis | Flow Rate (ACFM @ 250°F)
Blower Outlet Area (ft2) |  | 1.3 | [7 empty] | y - axis | S.P. (in wg)
ACFM @ 250°F | SP (in. wg) | Power (Hp)
0 | 6.2 | 1.25
500 | 6.6 | 1.75
1000 | 6.9 | 2.4
1500 | 7 | 2.7 | STEP 2: Populate Table of Coefficients |  |  |  |  | RESULTS
2000 | 6.65 | 3.15 | Use best fit trendlines to determine the equations describing power and pressure curves. |  |  |  |  | Includes Temperature Correction
2500 | 6 | 3.45 | [5 empty] | Flow rate ACFM (Q3) | 4364.717
3000 | 5.25 | 3.8 | Table of Coefficients (A = highest power) |  |  |  |  | Pressure (P2) | 0.5
3500 | 4.1 | 3.9 |  | A | B | C | D | Rpm (n3) | 2878.539
4000 | 2.8 | 3.75 | S.P. (P1) | -4.8298e-07 | 0.001104 | 6.257 |  | BHP3 | 3.3956
4500 | 1.2 | 3.5 | Power | -3.7918e-11 | 6.2704e-08 | 0.00098162 | 1.2689 | Outlet Ft/m (Actual) | 3357.4746
5000 | 0 | 3 | Note: solving for Q1 is easiest when S.P is quadratic |  |  |  |  | (red text is over limit)
|  |  | Step 3: Specify new Operating point |  |  |  |  | Step 5: Optional Inputs |  | Inlet Conditions
|  |  | Flow rate {SCFM} (Q2,std.) |  |  |  | 3300 | Dryer Bed Length (ft) | 6.4 | Inlet Temperature (°F,°C) |  | 45 | 7.2222
|  |  | Operating S.P. {inH20} (P2) |  |  |  | 0.5 | Dryer Bed Width (ft) | 2 | Inlet Diameter (Inch, m) |  | 20 | 0.508
|  |  | Operating Temp {°F} |  |  |  | 241 | Dryer Bed Area (ft2) | 12.8 | Inlet Area (ft2, m2) |  | 2.1817 | 0.20268
[8 empty] | Free Stream V (AFPM) | 340.9935 | Density Factor (Kd) |  | 0.95283
|  |  | Step 4: Calculate System Curve Intersection |  |  |  |  | Free Stream V (m/s) | 1.7322 | Inlet Volumetric flow (SCFM, SLPS) |  | 3300 | 1557.424
|  |  | From the System curve relationship (Eq. 1), solve for the flow rate in SCFM on the original fan curve (Q1). Recall that the static pressure (P1) on the original fan curve is give as a function of Q1 using the equation from Step 2. Use temperature corrected to flow rate for these calculations For example: If the pressure equation is quadratic and the power curve is cubic, then Q1 = (-B - sqrt(B2 - 4(A-P2/Q22)C) )/ 2(A-P2/Q22) P1 = AQ12 + BQ1 + C BHP1 = AQ13 + BQ12 + CQ1 + D | [6 empty] | Inlet Volumetric flow (ACFM, ALPS) |  | 3144.3396 | 1483.9606
[10 empty] | Inlet Velocity (FPM, MPS) |  | 1441.2591 | 7.3216
[8 empty] | Intermediate State |  | Inlet mass flow (lbs/s, kg/s) | Inlet Mass Flow (kg/s, lbs/s) | 4.1349 | 1.8756
Includes Temperature Correction
[8 empty] | Density Factor (Kd,1-2) | 0.74648
[8 empty] | Density Factor (Kd,2-3) | 1.3226 |  |  |  |  | `
(red text is over limit)
|  |  | Flow rate CFM (Q2,chart) |  |  | 4364.717
|  |  | P2/Q22 |  |  | 2.5913e-08
|  |  | Q1,chart |  |  | 4755.1041
|  |  | P1,chart |  |  | 0.58592
|  |  | BHP2,chart |  |  | 3.2775
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
Eq. 2: Rpm - flow relationship (41.22)
Eq. 3: Rpm - Pressure relationship (41.23)
Eq. 4: Rpm- Power Relationship (41.25)
Eq. 5 Density factor (absolute Temp) (41.2)
Eq. 6 Density flow change (41.1)
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
𝑃_1/𝑃_2 =(𝑄_1/𝑄_2 )^2
Eq. 2: Rpm - flow relationship (41.22)
𝑛_1/𝑛_2 =𝑄_1/𝑄_2
Eq. 3: Rpm - Pressure relationship (41.23)
(𝑛_1/𝑛_2 )^2=𝑃_1/𝑃_2
Eq. 4: Rpm- Power Relationship (41.25)
(𝑛_1/𝑛_2 )^3=〖𝐵𝐻𝑃〗_1/〖𝐵𝐻𝑃〗_2
Eq. 5 Density factor (absolute Temp) (41.2)
𝐾_𝑑=𝜌_𝑠𝑡𝑑/𝜌_𝑎𝑐𝑡 =𝜌_1/𝜌_2 =(𝑃_1/𝑃_2 )×(𝑇_2/𝑇_1 )
Eq. 6 Density flow change (41.1)
𝑆𝐶𝐹𝑀=𝐴𝐶𝐹𝑀/𝐾_𝑑
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
- Static Pressure (In w.g.)
- Power (HP)
- System Curve
- Power Intersection

## Hartzel A03-9-152BC-75STFCM 70F
FAN Brand | Hartzel
Model Number | A03-9-152BC-75STFCM2 | [8 empty] | System Curve Line, for graphic only
PURCHASED FOR USDA 2015 DRYER PHASE II | [9 empty] | zero | 0 | 0
[10 empty] | Point 1 | 4210.5563 | 0.31321 | Existing curve
STEP 1: Populate Chart | [9 empty] | Point 2 | 5192.9245 | 0.47642 | NEW point (TC)
Read data from the chart profided by the manufacturer. | [9 empty] | Power Curve Line, for graphic only
[10 empty] | zero | 5192.9245 | 0
[10 empty] | System Curve | 5192.9245 | 0.47642
Chart RPM (n1) |  | 2804 | [7 empty] | S.P. Curve | 5192.9245 | -5.018
Chart Temperature (°F) |  | 70 | [7 empty] | Power Curve | 5192.9245 | 1.4613
Maximum rated RPM |  | 3460 | [7 empty] | Chart Labels
Maximum Rated Temperature (°F) |  | 800 | [7 empty] | Title | Hartzel A03-9-152BC-75STFCM2
Motor Power (Hp) |  | 7.5 | [7 empty] | x - axis | Flow Rate (ACFM @ 70°F)
Blower Outlet Area (ft2) |  | 1.3 | [7 empty] | y - axis | S.P. (in wg)
ACFM @ 70°F | SP (in. wg) | Power (Hp)
0 | 6.2 | 1.25
500 | 7.2 | 1.7
1000 | 7.5 | 2.4
1500 | 7.5 | 2.7 | STEP 2: Populate Table of Coefficients |  |  |  |  | RESULTS
2000 | 6.85 | 3.125 | Use best fit trendlines to determine the equations describing power and pressure curves. |  |  |  |  | Includes Temperature Correction
2500 | 6 | 3.6 | [5 empty] | Flow rate ACFM (Q3) | 5192.9245
3000 | 4.6 | 3.75 | Table of Coefficients (A = highest power) |  |  |  |  | Pressure (P2) | 0.5
3500 | 3.25 | 3.6 |  | A | B | C | D | Rpm (n3) | 3458.2034
4000 | 1.4 | 3.4 | S.P. (P1) | -7.6775e-07 | 0.0017927 | 6.3764 |  | BHP3 | 5.9693
4500 |  |  | Power | -5.9596e-11 | 1.3463e-07 | 0.0009491 | 1.2477 | Outlet Ft/min (Actual) | 3994.5573
5000 |  |  | Note: solving for Q1 is easiest when S.P is quadratic |  |  |  |  | (red text is over limit)
|  |  | Step 3: Specify new Operating point |  |  |  |  | Step 5: Optional Inputs |  | Inlet Conditions
|  |  | Flow rate {SCFM} (Q2,std.) |  |  |  | 5450 | Dryer Bed Length (ft) | 5 | Inlet Temperature (°F,°C) |  | 45 | 7.2222
|  |  | Operating S.P. {inH20} (P2) |  |  |  | 0.5 | Dryer Bed Width (ft) | 2 | Inlet Diameter (Inch, m) |  | 20 | 0.508
|  |  | Operating Temp {°F} |  |  |  | 45 | Dryer Bed Area (ft2) | 10 | Inlet Area (ft2, m2) |  | 2.1817 | 0.20268
[8 empty] | Free Stream V (AFPM) | 519.2925 | Density Factor (Kd) |  | 0.95283
|  |  | Step 4: Calculate System Curve Intersection |  |  |  |  | Free Stream V (m/s) | 2.638 | Inlet Volumetric flow (SCFM, SLPS) |  | 5450 | 2572.1093
|  |  | From the System curve relationship (Eq. 1), solve for the flow rate in SCFM on the original fan curve (Q1). Recall that the static pressure (P1) on the original fan curve is give as a function of Q1 using the equation from Step 2. Use temperature corrected to flow rate for these calculations For example: If the pressure equation is quadratic and the power curve is cubic, then Q1 = (-B - sqrt(B2 - 4(A-P2/Q22)C) )/ 2(A-P2/Q22) P1 = AQ12 + BQ1 + C BHP1 = AQ13 + BQ12 + CQ1 + D | [6 empty] | Inlet Volumetric flow (ACFM, ALPS) |  | 5192.9245 | 2450.7834
[10 empty] | Inlet Velocity (FPM, MPS) |  | 2380.2613 | 12.0917
[8 empty] | Intermediate State |  | Inlet mass flow (lbs/s, kg/s) | Inlet Mass Flow (kg/s, lbs/s) | 6.8288 | 3.0975
Includes Temperature Correction
[8 empty] | Density Factor (Kd,1-2) | 1
[8 empty] | Density Factor (Kd,2-3) | 0.95283
(red text is over limit)
|  |  | Flow rate CFM (Q2,Actual) |  |  | 5192.9245
|  |  | P2/Q22 |  |  | 1.7667e-08
|  |  | Q1,chart |  |  | 4210.5563
|  |  | P1,chart |  |  | 0.31321
|  |  | BHP2,chart |  |  | 3.182
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
Eq. 2: Rpm - flow relationship (41.22)
Eq. 3: Rpm - Pressure relationship (41.23)
Eq. 4: Rpm- Power Relationship (41.25)
Eq. 5 Density factor (absolute Temp) (41.2)
Eq. 6 Density flow change (41.1)
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
Useful Equations
(source: PE Ref Manaul)
Eq. 1: System Curve relationship (41.21)
𝑃_1/𝑃_2 =(𝑄_1/𝑄_2 )^2
Eq. 2: Rpm - flow relationship (41.22)
𝑛_1/𝑛_2 =𝑄_1/𝑄_2
Eq. 3: Rpm - Pressure relationship (41.23)
(𝑛_1/𝑛_2 )^2=𝑃_1/𝑃_2
Eq. 4: Rpm- Power Relationship (41.25)
(𝑛_1/𝑛_2 )^3=〖𝐵𝐻𝑃〗_1/〖𝐵𝐻𝑃〗_2
Eq. 5 Density factor (absolute Temp) (41.2)
𝐾_𝑑=𝜌_𝑠𝑡𝑑/𝜌_𝑎𝑐𝑡 =𝜌_1/𝜌_2 =(𝑃_1/𝑃_2 )×(𝑇_2/𝑇_1 )
Eq. 6 Density flow change (41.1)
𝑆𝐶𝐹𝑀=𝐴𝐶𝐹𝑀/𝐾_𝑑
NOTE (pg. 41-11): Fans are constant-volume devices. They deliver the same volume of air (and at the same duct speed) regardless of temperature, pressure, and humidity ratio. Therefore, the actual flow rate, ACFM should be used to select a fan from rating tables. The speed can be read directly from the fan table. The table values of power and pressure should be modified by the density factor Kd.
- Static Pressure (In w.g.)
- Power (HP)
- System Curve
- Power Intersection